## Slide 1: Smart Grid Final Project
PROJECT OPTION: SELF-PROPOSED NETWORK
Presented by: Haocong Wang
Dazhi Li

## Slide 2: Network Details
Slack Bus: 1
PV Bus: 3
PQ Bus: 7
Total: 11 Buses
4 Transformers:
T1
T2
T3
T4
Transformers | Rated Power(MVA) | Voltage ratio: K=1 | ZT
T1 | 900 | 1 | j0.15
T2 | 900 | 1 | j0.15
T3 | 900 | 1 | j0.15
T4 | 900 | 1 | j0.15
Sbase=100MVA

## Slide 3: Line Info (Given)
Line | Distance（km） | ro(p.u/km) | xo(p.u/km) | bo(p.u/km)
L56 | 25 | 0.0001 | 0.001 | 0.00175
L67 | 10 | 0.0001 | 0.001 | 0.00175
L78 | 110 | 0.0001 | 0.001 | 0.00175
L89 | 110 | 0.0001 | 0.001 | 0.00175
L9-10 | 10 | 0.0001 | 0.001 | 0.00175
L10-11 | 25 | 0.0001 | 0.001 | 0.00175
Capacitors’ Susceptance:
C7=j2.1 ; C9=j3.6

## Slide 4: Bus Info (Given)
Bus | Type | P | Q | ¦V¦ | θ(degree)
1 | PV | 7.00 |  | 1.03 | 
2 | PV | 7.00 |  | 1.01 | 
3 | Slack |  |  | 1.03 | 0.0
4 | PV | 7.00 |  | 1.01 | 
5 | PQ | 0.00 | 0.00 |  | 
6 | PQ | 0.00 | 0.00 |  | 
7 | PQ | 9.67 | 1.00 |  | 
8 | PQ | 0.00 | 0.00 |  | 
9 | PQ | 17.67 | 1.00 |  | 
10 | PQ | 0.00 | 0.00 |  | 
11 | PQ | 0.00 | 0.00 |  | 

## Slide 5: Initial Guess & Y Admittance Matrix
All PV bus with voltage angle = 0
All PQ bus with |voltage| = 1, Angle = 0°
3.9604-j99.582 | -3.9604+j39.604 |  |  |  |  |  | 0+j60 |  |  | 
-3.9604+j39.604 | 13.861-j198.58 | -9.901+j99.01 |  |  |  |  |  | 0+j60 |  | 
 | -9.901+j99.01 | 11.701-j114.71 | -1.8002+j18.002 |  |  |  |  |  |  | 
 |  | -1.8002+j18.002 | 3.6004-j35.619 | -1.8002+j18.002 |  |  |  |  |  | 
 |  |  | -1.8002+j18.002 | 11.701-j113.21 | -9.901+j99.01 |  |  |  |  | 
 |  |  |  | -9.901+j99.01 | 13.861-j198.58 | -3.9604+j39.604 |  |  | 0+j60 | 
 |  |  |  |  | -3.9604+j39.604 | 3.9604-j99.582 |  |  |  | 0+j60
0+j60 |  |  |  |  |  |  | 0-j60 |  |  | 
 | 0+j60 |  |  |  |  |  |  | 0-j60 |  | 
 |  |  |  |  | 0+j60 |  |  |  | 0-j60 | 
 |  |  |  |  |  | 0+j60 |  |  |  | 0-j60
Y=

## Slide 6: Gauss-Seidal Result
Bus | ¦Voltage¦ | Angle (Degree) | Complex
1 | 1.0300 | -1.5690 | 1.0300 - j0.0019
2 | 1.0100 | -1.5689 | 1.0100 - j0.0019
3 | 1.0300 | 0 | 1.0300 + j0.0000
4 | 1.0100 | -1.5689 | 1.0100 - j0.0019
5 | 1.0004 | -1.6244 | 0.9989 - j0.0536
6 | 0.9487 | -1.7116 | 0.9393 - j0.1331
7 | 0.8885 | -1.8477 | 0.8547 - j0.2429
8 | 0.5714 | -2.0561 | 0.5054 - j0.2665
9 | 0.2275 | 3.0700 | 0.2270 + j0.0163
10 | 0.3340 | -1.6011 | 0.3338 - j0.0101
11 | 0.6433 | -0.2481 | 0.6236 - j0.1580

## Slide 7: Newton-Raphson Result
Bus | ¦Voltage¦ | Angle (Degree) | P + jQ
1 | 1.03 | 26.922 | 7 + j1.810
2 | 1.01 | 17.168 | 7 + j2.250
3 | 1.03 | 0 | 7.187 + j1.716
4 | 1.01 | -10.171 | 7 + j1.918
5 | 1.0071 | 20.464 | 0
6 | 0.9797 | 10.397 | 0
7 | 0.9638 | 2.019 | -9.670 - j1
8 | 0.9518 | -11.770 | 0
9 | 0.9744 | -25.285 | -17.670 - j1
10 | 0.9851 | -16.904 | 0
11 | 1.0090 | -6.619 | 0

## Slide 8: Current Result
Bus I | Bus J | Current (From I to J) | Current (From J to I)
1 | 5 | 6.855294 + j1.510179 | -6.855294 - j1.510179
5 | 6 | 6.855294 + j1.510179 | -6.866864 - j1.468460
2 | 6 | 7.279377 - j0.082425 | -7.279377 + j0.082425
6 | 7 | 14.146241 + j1.386035 | -14.148085 - j1.369174
7 | 8 | 2.078187 + j0.014903 | -2.062768 + j0.167495
8 | 9 | 2.062768 - j0.167495 | -2.004024 + j0.341979
9 | 10 | -13.449209 + j4.818059 | 13.455357 - j4.80210
4 | 10 | 6.486440 - j3.093086 | -6.486440 + j3.093086
10 | 11 | -6.968917 + j1.709016 | 6.977727 - j1.666474
3 | 11 | 6.977727 - j1.666474 | -6.977727 + j1.666474
7 | 0 | -0.071299 + j2.022827 | 0
9 | 0 | 1.498220 + j3.171676 | 0

## Slide 9: Power Flow Result
Bus I | Bus J | S (From I to J) | S (From J to I) | Line Loss S
1 | 5 | 7.000000 + j1.810135 | -7.000000 - j0.988874 | 0.000000 + j0.821262
5 | 6 | 7.000000 + j0.988874 | -6.876701 + j0.200930 | 0.123299 + j1.189803
2 | 6 | 7.000000 + j2.249742 | -7.000000 - j1.366474 | 0.000000 + j0.883269
6 | 7 | 13.876701 + j1.165544 | -13.674644 + j0.838505 | 0.202058 + j2.004050
7 | 8 | 2.002322 + j0.056203 | -1.954598 + j0.244420 | 0.047724 + j0.300623
8 | 9 | 1.954598 - j0.244420 | -1.907910 + j0.532728 | 0.046688 + j0.288309
9 | 10 | -13.854180 + j1.352375 | 14.058299 + j0.672013 | 0.204119 + j2.024387
4 | 10 | 7.000000 + j1.918092 | -7.000000 - j1.057407 | 0.000000 + j0.860685
10 | 11 | -7.058299 + j0.385394 | 7.187059 + j0.858704 | 0.128760 + j1.244098
3 | 11 | 7.187059 + j1.716468 | -7.187059 - j0.858704 | 0.000000 + j0.857763
7 | 0 | 0.000000 - j1.950911 | 0 | 0.000000 - j1.950911
9 | 0 | 0.000000 - j3.417832 | 0 | 0.000000 - j3.417832

## Slide 10: One-Line Fault Analysis
We choose to delete the Bus 5, and the new electrical network is:
Slack Bus: 1
PV Bus: 3
PQ Bus: 6
Total: 10 Buses
4 Transformers:
Transformers | Rated Power(MVA) | Voltage ratio: K=1 | ZT
T1 | 900 | 1 | j0.15
T2 | 900 | 1 | j0.15
T3 | 900 | 1 | j0.15
T4 | 900 | 1 | j0.15
Sbase=100MVA
Other initial conditions remain the same: line & bus info

## Slide 11: One-Line Fault Result: Newton-Raphson
Bus | ¦Voltage¦ | Angle (Degree) | P + jQ
1 | 1.03 | 37.135541 | 7 + j2.419799
2 | 1.01 | 37.265257 | 7 + j1.176506
3 | 1.03 | 0 | 7.073890 + j1.498509
4 | 1.01 | -9.845945 | 7 + j1.457941
6 | 0.997298 | 30.614072 | 0
7 | 0.973899 | 22.440945 | -9.67 - j1
8 | 0.932464 | -6.768899 | 0
9 | 0.987512 | -20.604789 | -17.67 - j1
10 | 0.992685 | -16.528177 | 0
11 | 1.012245 | -6.492871 | 0

## Slide 12: One-Line Fault Result: Current
Bus I | Bus J | Current (From I to J) | Current (From J to I)
1 | 6 | 6.836220 + j2.229933 | -6.836220 - j2.229933
2 | 6 | 6.221057 + j3.269534 | -6.221057 - j3.269534
6 | 7 | 13.057276 + j5.499468 | -13.064973 - j5.484081
7 | 8 | 4.276466 + j0.752545 | -4.301671 - j0.576781
8 | 9 | 2.150835 + j0.288391 | -2.106808 - j0.110299
9 | 10 | -6.714961 + j2.068952 | 6.720473 - j2.052537
4 | 10 | 6.581772 - j2.607391 | -6.581772 + j2.607391
10 | 11 | -6.859173 + j1.497682 | 6.867854 - j1.454864
3 | 11 | 6.867854 - j1.454864 | -6.867854 + j1.454864
7 | 0 | -0.780712 + j1.890314 | 0
9 | 0 | 1.251090 + j3.327626 | 0

## Slide 13: One-Line Fault Result: Power Flow
Bus I | Bus J | S (From I to J) | S (From J to I) | Line Loss S
1 | 6 | 7.000000 + j2.419799 | -7.000000 - j1.558024 | 0.000000 + j0.861775
2 | 6 | 7.000000 + j1.176506 | -7.000000 - j0.353316 | 0.000000 + j0.823190
6 | 7 | 14.000000 + j1.911340 | -13.799230 + j0.079359 | 0.200770 + j1.990699
7 | 8 | 4.129230 + j0.912449 | -3.919802 + j1.006853 | 0.209428 + j1.919302
8 | 9 | 1.959901 - j0.503427 | -1.909076 + j0.834122 | 0.050824 + j0.330695
9 | 10 | -6.925924 + j0.421201 | 6.975302 + j0.055431 | 0.049379 + j0.476632
4 | 10 | 7.000000 + j1.457941 | -7.000000 - j0.622638 | 0.000000 + j0.835304
10 | 11 | -6.950605 + j0.511775 | 7.073890 + j0.677109 | 0.123285 + j1.188884
3 | 11 | 7.073890 + j1.498509 | -7.073890 - j0.677109 | 0.000000 + j0.821401
7 | 0 | 0.000000 - j1.991808 | 0 | 0.000000 - j1.991808
9 | 0 | 0.000000 - j3.510645 | 0 | 0.000000 - j3.510645

## Slide 14: Comparison
Compared to the original grid, there are some changes in the new grid.
For each PQ bus (6-11), the absolute value of voltage slightly increases while the phase value changes a lot.
For the slack bus and all the PV buses (1-4), the phase value of voltage and input power changes a little bit.
For the power flow changes in each line, if the line is closer to the deleted bus, the changes in the power flow, line losses and line current will be greater.
In summary, the failure of bus 5 does not cause significant changes in the new system.